## GW SG1 + Telepuerto Backup
NO ESCENCIAL UP-1 SG1 | [5 empty] | C/GW
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H |  | NO ESCENCIAL | 150.9
Utility Loads | [7 empty] | ESCENCIAL | 101.27
Deice system | 34 | 380 | UP-1 | 0.8 | 27200 | 92810.2524
Antenna Driving power | 25 | 380 | UP-1 | 0.8 | 20000 | 68242.8327
Aircraft warning lights | 0.1 | 220 | UP-1 | 0.8 | 80 | 272.9713 |  | BTU de Refrigeracion
Antenna lights | 0.5 | 220 | UP-1 | 0.8 | 400 | 1364.8567 |  | total | 322433.7358
Antenna receptacles | 2 | 220 | UP-1 | 0.8 | 1600 | 5459.4266
Jackscrew Gear Box Htr Assy | 0.75 | 220 | UP-1 | 0.8 | 600 | 2047.285 |  | Power Factor | 0.8
Hoist | 2 | 220 | UP-1 | 0.8 | 1600 | 5459.4266
ECU1 (3 Tons) | 12.5 | 380 | UP-1 | 0.8 | 10000 | 34121.4163
ECU2 (3 Tons) | 12.5 | 380 | UP-1 | 0.8 | 10000 | 34121.4163
Feed Blower | 0.7 | 220 | UP-1 | 0.8 | 560 | 1910.7993
PANEL UP-1 CONNECTED LOAD | 90.05 |  |  | TOTAL BTU |  | 245810.6832 | NO SE SUMA AL TOTAL DE BTU
NO ESCENCIAL AR-1
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
Utility Loads
Antenna Driving power | 15 | 380 |  | 0.8 | 12000 | 40945.6996
Aircraft warning lights | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Antenna lights | 0.5 | 220 |  | 0.8 | 400 | 1364.8567
Antenna receptacles | 2 | 220 |  | 0.8 | 1600 | 5459.4266
Hoist | 2 | 220 |  | 0.8 | 1600 | 5459.4266
AA | 2 | 220 |  | 0.8 | 1600 | 5459.4266
Feed Blower | 0.7 | 220 |  | 0.8 | 560 | 1910.7993
PANEL UP-1 CONNECTED LOAD | 22.3 |  |  | TOTAL BTU |  | 60872.6067 | NO SE SUMA AL TOTAL DE BTU
NO ESCENCIAL AR-2
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
Utility Loads
Antenna Driving power | 15 | 380 |  | 0.8 | 12000 | 40945.6996
Aircraft warning lights | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Antenna lights | 0.5 | 220 |  | 0.8 | 400 | 1364.8567
Antenna receptacles | 2 | 220 |  | 0.8 | 1600 | 5459.4266
Hoist | 2 | 220 |  | 0.8 | 1600 | 5459.4266
AA | 2 | 220 |  | 0.8 | 1600 | 5459.4266
Feed Blower | 0.7 | 220 |  | 0.8 | 560 | 1910.7993
PANEL UP-1 CONNECTED LOAD | 22.3 |  |  | TOTAL BTU |  | 60872.6067 | NO SE SUMA AL TOTAL DE BTU
ESCENCIAL TP-1A & TP-1B
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
UPS LOADS
PDU Control Power | 0.7 | 220 | TP-1A | 0.8 | 560 | 1910.7993
HPA 1 | 1.25 | 220 | TP-1A | 0.8 | 1000 | 3412.1416
HPA 3 | 1.25 | 220 | TP-1A | 0.8 | 1000 | 3412.1416
Switched PDU 1 (Phase A) | 0.5 | 220 | TP-1A | 0.8 | 400 | 1364.8567
BUC1 | 0.1 | 220 |  | 0.8 | 80 | 272.9713
BDC1 | 0.1 | 220 |  | 0.8 | 80 | 272.9713
BUC3 | 0.1 | 220 |  | 0.8 | 80 | 272.9713
BDC3 | 0.1 | 220 |  | 0.8 | 80 | 272.9713
TLT | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Switched PDU 2 (Phase B) | 0.67 | 220 | TP-1A | 0.8 | 536 | 1828.9079
HUB M&C PS1 | 0.18 | 220 |  | 0.8 | 144 | 491.3484
Signal Generator | 0.29 | 220 |  | 0.8 | 232 | 791.6169
10MHz Dist AMP | 0.2 | 220 |  | 0.8 | 160 | 545.9427
HPA 2 (Ka-Band) | 1.25 | 220 | TP-1B | 0.8 | 1000 | 3412.1416
HUB Power strip (phase C) | 2.07 | 220 | TP-1B | 0.8 | 1656 | 5650.5065
BUC2 | 0.1 | 220 |  | 0.8 | 80 | 272.9713
BDC2 | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Tx BDC | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Monopulse | 0.2 | 220 |  | 0.8 | 160 | 545.9427
HUB M&C PS2 | 0.18 | 220 |  | 0.8 | 144 | 491.3484
Tx. Warning Light | 0.01 | 220 |  | 0.8 | 8 | 27.2971
2 Outlets | 1.4 | 220 | TP-1B | 0.8 | 1120 | 3821.5986
HUB cooling conrtoller | 0.4 | 220 | TP-1B | 0.8 | 320 | 1091.8853
IF & BB RACK POWER STRIP 1 | 2.5 | 220 | TP-1A | 0.8 | 2000 | 6824.2833
IF & BB RACK POWER STRIP 2 | 1.8 | 220 | TP-1B | 0.8 | 1440 | 4913.484
CSM RACK POWER STRIP 1 | 1.25 | 220 | TP-1A | 0.8 | 1000 | 3412.1416
CSM RACK POWER STRIP 2 | 1.25 | 220 | TP-1B | 0.8 | 1000 | 3412.1416
Access Control system |  |  |  | 0.8 | 0 | 0
PANEL TP-1 CONNECTED LOAD | 18.15 |  |  | TOTAL BTU |  | 49544.2965
NO ESCENCIAL UP-2
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
RF EQUIPMENT ROOM
AAx4 | 15.2 | 380 |  | 0.8 | 12160 | 41491.6423
ACU/M&C rack Dehydrator #1 & #2 | 0.3 | 380 | UP-2 | 0.8 | 240 | 818.914
Sistema de incendios | 0.5 |  |  | 0.8 | 400 | 1364.8567
Central de incendios | 0.25 |  |  | 0.8 | 200 | 682.4283
PANEL UP-1 CONNECTED LOAD = | 16.25 |  |  | TOTAL BTU |  | 44357.8412
ESCENCIAL TP-2
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
ACU/M&C rack pwr strip #1 & #2 | 1.64
Gps Receiver | 0.1 | 220 | TP-1A | 0.8 | 80 | 272.9713
Deice control | 0.2 | 220 | TP-1A | 0.8 | 160 | 545.9427
LNA control | 0.1 | 220 | TP-1A | 0.8 | 80 | 272.9713
ATS |  | 220 | TP-1A | 0.8 | 0 | 0
Beacon Receiver | 0.24 | 220 |  | 0.8 | 192 | 655.1312
ACU | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Serial Interface Hub | 0.05 | 220 |  | 0.8 | 40 | 136.4857
KVM & Monitor | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Ethernet | 0.05 | 220 |  | 0.8 | 40 | 136.4857
M&C GUI Server | 0.2 | 220 | TP-1A | 0.8 | 160 | 545.9427
System Main Server | 0.25 | 220 |  | 0.8 | 200 | 682.4283
System Back Up Server | 0.25 | 220 |  | 0.8 | 200 | 682.4283
UPLINK RACK PWR STRIP #1 & #2 | 0.5 | 220 |  | 0.8 | 400 | 1364.8567
Line driver 1 | 0.05 | 220 | TP-1B | 0.8 | 40 | 136.4857
Line driver 2 | 0.05 | 220 | TP-1B | 0.8 | 40 | 136.4857
Line driver 3 | 0.05 | 220 |  | 0.8 | 40 | 136.4857
Line driver 4 | 0.05 | 220 |  | 0.8 | 40 | 136.4857
Line driver 5 | 0.05 | 220 |  | 0.8 | 40 | 136.4857
Line driver 6 | 0.05 | 220 |  | 0.8 | 40 | 136.4857
Line driver 7 | 0.05 | 220 |  | 0.8 | 40 | 136.4857
Uplink L-Ban 16x8 Matrix SW | 0.1 | 220 |  | 0.8 | 80 | 272.9713
L-Band signal Generator | 0.05 | 220 |  | 0.8 | 40 | 136.4857
PANEL TP-1 CONNECTED LOAD = | 4.28 |  |  | TOTAL BTU |  | 7206.4431
ESCENCIAL IT&BB
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
Nodos x 12 | 6 | 220 |  | 0.8 | 4800 | 16378.2798
CTX x 6 | 6 | 220 |  | 0.8 | 4800 | 16378.2798
Switch Matrix QRM DL | 0.08 | 220 |  | 0.8 | 64 | 218.3771
Switch Matrix QRM UL | 0.08 |  |  | 0.8 | 64 | 218.3771
Cisco 3750 x 4 | 2 |  |  | 0.8 | 1600 | 5459.4266
FW x 4 | 2 |  |  | 0.8 | 1600 | 5459.4266
SW 2960 x 6 | 4.5 |  |  | 0.8 | 3600 | 12283.7099
Replication Server | 0.7 |  |  | 0.8 | 560 | 1910.7993
PCS | 2 |  |  | 0.8 | 1600 | 5459.4266
STORAGE STORMWIZE x 4 | 7.5 |  |  | 0.8 | 6000 | 20472.8498
XENSERVER x 2 | 6.5 |  |  | 0.8 | 5200 | 17743.1365
Cisco 9300 x 4 | 3 |  |  | 0.8 | 2400 | 8189.1399
TV 55" x 4 | 0.22 |  |  | 0.8 | 176 | 600.5369
PANEL TP-1 CONNECTED LOAD = | 40.58 |  |  | TOTAL BTU |  | 110771.766
ESCENCIAL TTC
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
IF & BB RACK POWER STRIP 1 | 2.5 | 220 |  | 0.8 | 2000 | 6824.2833
IF & BB RACK POWER STRIP 2 | 1.8 |  |  | 0.8 | 1440 | 4913.484
IF & BB RACK FAN | 0.5 |  |  | 0.8 | 400 | 1364.8567
CSM RACK POWER STRIP 1 | 1.25 |  |  | 0.8 | 1000 | 3412.1416
CSM RACK POWER STRIP 2 | 1.25 |  |  | 0.8 | 1000 | 3412.1416
CSM RACK FAN | 0.5 |  |  | 0.8 | 400 | 1364.8567
ACU RACK POWER STRIP 1 | 1.54 |  |  | 0.8 | 1232 | 4203.7585
ACU RACK POWER STRIP 2 | 1.54 |  |  | 0.8 | 1232 | 4203.7585
ACU RACK FAN | 0.5 |  |  | 0.8 | 400 | 1364.8567
HPA RACK (HPA 1) | 5.04 |  |  | 0.8 | 4032 | 13757.7551
HPA RACK (HPA 2) | 5.04 |  |  | 0.8 | 4032 | 13757.7551
HPA RACK FAN | 0.5 |  |  | 0.8 | 400 | 1364.8567
RF RACK POWER STRIP 1 | 0.31 |  |  | 0.8 | 248 | 846.2111
RF RACK POWER STRIP 2 | 0.31 |  |  | 0.8 | 248 | 846.2111
RF RACK FAN | 0.5 |  |  | 0.8 | 400 | 1364.8567
PDU logic | 0.6 |  |  | 0.8 | 480 | 1637.828
PANEL TP-1 CONNECTED LOAD = | 21.18 |  |  | TOTAL BTU |  | 64639.6111
ESCENCIAL SERVICIOS AR-1
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
U/C HPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C VPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C BUP | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C SW | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C HPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C VPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C BUP | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C SW | 0.03 | 220 |  | 0.8 | 24 | 81.8914
UPC | 0.04 | 220 |  | 0.8 | 32 | 109.1885
10MHz Dist | 0.02 | 220 |  | 0.8 | 16 | 54.5943
Dehydrator | 0.1 | 220 |  | 0.8 | 80 | 272.9713
LNA CTLR | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Fei-Zyfer | 0.15 | 220 |  | 0.8 | 120 | 409.457
TWT | 2.5 | 380 |  | 0.8 | 2000 | 6824.2833
TWT | 2.5 | 380 |  | 0.8 | 2000 | 6824.2833
TWT | 2.5 | 380 |  | 0.8 | 2000 | 6824.2833
TWT Cooler | 0.02 | 220 |  | 0.8 | 16 | 54.5943
D/C HPOL 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C VPOL 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
TLT | 0.05 | 220 |  | 0.8 | 40 | 136.4857
U/C 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
PANEL TP-1 CONNECTED LOAD = | 8.34 |  |  | TOTAL BTU |  | 22274.4606
ESCENCIAL SERVICIOS AR-1
Equipment / Location | Power required | Voltage required | Power Source | Power Factor | VA | HEAT HOUR BTU/H
U/C HPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C VPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C BUP | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C SW | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C HPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C VPOL | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C BUP | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C SW | 0.03 | 220 |  | 0.8 | 24 | 81.8914
UPC | 0.04 | 220 |  | 0.8 | 32 | 109.1885
10MHz Dist | 0.02 | 220 |  | 0.8 | 16 | 54.5943
Dehydrator | 0.1 | 220 |  | 0.8 | 80 | 272.9713
LNA CTLR | 0.1 | 220 |  | 0.8 | 80 | 272.9713
Fei-Zyfer | 0.15 | 220 |  | 0.8 | 120 | 409.457
TWT | 2.5 | 380 |  | 0.8 | 2000 | 6824.2833
TWT | 2.5 | 380 |  | 0.8 | 2000 | 6824.2833
TWT | 2.5 | 380 |  | 0.8 | 2000 | 6824.2833
TWT Cooler | 0.02 | 220 |  | 0.8 | 16 | 54.5943
D/C HPOL 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
D/C VPOL 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
TLT | 0.05 | 220 |  | 0.8 | 40 | 136.4857
U/C 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
U/C 70 MHz | 0.03 | 220 |  | 0.8 | 24 | 81.8914
PANEL TP-1 CONNECTED LOAD = | 8.34 |  |  | TOTAL BTU |  | 22765.809
ESCENCIAL SERVICIOS AR1&2
Equipment / Location | Power required | Voltage required | Power Source
Switch Matrix QRM | 0.08 | 220 |  | Power Factor | VA | HEAT HOUR BTU/H
Switch Matrix QRF | 0.08 | 220 |  | 0.8 | 64 | 218.3771
MODULATOR #1 | 0.12 | 220 |  | 0.8 | 96 | 327.5656
MODULATOR #2 | 0.12 | 220 |  | 0.8 | 96 | 327.5656
PANEL TP-1 CONNECTED LOAD = | 0.4 |  |  | TOTAL BTU |  | 873.5083
Note on H72: Moruga Gabriel: